## Sheet1
VITA Contract VA-220218-FPI - Exhibit A - Cabling Requirements
I. | Exhibit A: REQUIREMENTS
A. Services: It is the intent of this solicitation that the Contractor supply hourly labor rates, by District, for Services to include labor, and all incidental materials, for installing the structured cabling Products specified herein as ordered by the Authorized Users. Separate hourly rates are required for each of the following Services:
1) Installation, termination and testing of horizontal twisted pair cabling and any other Category 5e and higher performance TIA-568-compliant copper cabling,
2) Installation, termination and testing of fiber optic cabling, and
3) Other cabling services to include but not be limited to the installation, termination and testing of Category 3 backbone cabling and coaxial cabling, performance of miscellaneous cabling services (see section II.E) and removal of abandoned cabling (see section II.F).
4) Each of these hourly labor rates must incorporate all labor costs associated with the provisioning and installation of the Products, and incidental materials costs specified herein including tools, ties , testing, documentation and any other incidental materials required to provide a turnkey cabling solution, but not including the cost of the items for which separate pricing is required in the schedule, including but not limited to the actual copper and fiber cables, connecting blocks, jacks, faceplates, patch cords, innerduct, racks, fiber cabinets, patch panels and plywood backboards themselves.
C. Products: The structured cabling Products referenced herein may only be ordered in conjunction with one or more of the above listed Services.
D. The Authorized User (AU) reserves the right to negotiate a Statement of Work (SOW) for any and all cabling work relating to an AU's Request for Quote (RFQ) for a contract purchase/project. Negotiated pricing may reduce the rates herein only for the scope of the particular project, as mutually agreed upon by the Supplier and the Authorized User in the SOW.
E. All standards and codes referenced in this document are adopted as part of this document and all Contractors shall comply with those standards and codes, including any advisory requirements contained in those standards and codes, unless it can be documented that those advisory requirements are impracticable with regard to the situation at hand and the Authorized User has authorized a deviation from those requirements in writing.
F. Warranties: Services shall be performed by fully-qualified individuals with all training and/or certification(s) required by the manufacturer(s) of the products used to deliver turnkey structured cabling systems to include any warranty/warranties offered by such manufacturer(s). Contractor shall provide all manufacturers’ warranties applicable to products delivered/installed to ordering Authorized User. All Services shall be warranted for 90 days.
II. | SCOPE OF WORK
A. General Requirements
1. The Contractor shall furnish all necessary labor, supervision, tools, materials, and testing as may be required to install structured cabling systems that comply with the TIA-568 “suite” of cabling standards, including but not limited to certified Enhanced Category 5 (“Category 5e”), Category 6, Category 6A, and/or fiber optic cabling systems, and/or coaxial cabling systems. TIA-568 is a set of telecommunications cabling and infrastructure standards from the Telecommunications Industry Association (TIA). The standards address building cabling and related infrastructure (e.g., pathways and spaces) for telecommunications products and services.
2. All cabling shall be delivered and installed as a turnkey system. This may include but not be limited to services such as providing and installing complete telecommunications cabling systems for new construction, cross-connecting new backbone cabling to existing horizontal cabling for voice and data, cross-connecting new horizontal cabling to backbone cabling, etc.
3. All work performed under this Contract shall be performed in accordance with the most recent versions of the applicable standards listed below and any addenda and revisions thereto, as amended.
a) Virginia Uniform Statewide Building Code
b) National Electric Code (NEC): ANSI/NFPA-70
c) Uniform Commercial Building Code
d) Safety Codes Commission of the Commonwealth of Virginia rules, issued by the Department of Labor and Industry under Title 40.1 of the Code of Virginia.
e) TIA-569, Telecommunications Pathways and Spaces
f) TIA-606, Administration Standard for Telecommunications Infrastructure
g) TIA-607, Generic Telecommunications Bonding and Grounding (Earthing) for Customer Premises
h) TIA-758, Customer-owned Outside Plant Telecommunications Infrastructure Standard
i) TIA-568.0, Generic Telecommunications Cabling for Customer Premises
j) TIA-568.1, Commercial Building Telecommunications Infrastructure Standard
k) TIA-568.2, Balanced Twisted-Pair Telecommunications Cabling and Components Standards
l) TIA-568.3, Optical Fiber Cabling and Components Standard
m) TIA-568.4, Broadband Coaxial Cabling and Components Standard
n) TIA-570, Residential Telecommunications Infrastructure Standard
o) TIA-598, Optical Fiber Cable Color Coding
p) TIA-526-7, Measurement of Optical Power Loss of Installed Single-Mode Fiber Cable Plant, Adoption of IEC 61280-4-2 edition 2: Fibre-Optic Communications Subsystem Test Procedures – Part 4-2: Installed Cable Plant – Single-Mode Attenuation and Optical Return Loss Measurement
q) TIA-526-14, Optical Power Loss Measurement of Installed Multimode Fiber Cable Plant; Modification of IEC 61280-4-1 edition 2, Fiber-Optic Communications Subsystem Test Procedures- Part 4-1: Installed Cable Plant-Multimode Attenuation Measurement
Note: Hereafter within this document, TIA-568.0, TIA-568.1, TIA-568.2, TIA-568.3 and TIA-568.4 and any revisions and addenda thereto will be collectively referred to simply as TIA-568.
4. All cables, ties, support hardware, and other miscellaneous devices used for the installation of the wiring and connectors shall be fully compliant with all applicable building codes.
5. The Contractor shall be responsible for ensuring that all cables maintain the appropriate minimum separation from all sources of EMI/RFI (light ballasts, motors, etc.).
6. The Contractor shall plan and coordinate the performance of all work with the Authorized User’s representative to minimize the impact of the work on the office environment and ongoing work activities, prevent the disruption of finished surfaces, and complete work in an orderly and expeditious manner. Where the work is to be performed in a new construction or renovation environment, the Contractor shall also coordinate with the Authorized User’s designated construction project manager to ensure that all work is performed in coordination with ongoing construction activities in such a manner as to cause the least possible disruption to finished surfaces and to facilitate the orderly and efficient completion of work.
7. Work shall be performed by competent technicians who are employees of the Contractor familiar with the specific equipment to be installed. The Contractor shall be responsible for initiating, maintaining, and supervising all safety precautions and programs in connection with the work.
8. The Contractor shall repair, to the Authorized User’s representative’s satisfaction, any damage to existing utilities, equipment, or finished surfaces resulting from this installation within 24 hours at the Contractor’s sole expense.
9. All debris generated by the Contractor shall be picked up and lawfully disposed of at the conclusion of each work day.
10. When providing cabling through conduit traversing a firewall, or in any other instance where devices transit a firewall or other fire-rated structure, the Contractor shall meet all codes and requirements for proper fire-stop materials and methods.
11. Bidder responses to requirements and specifications of the IFB shall be verifiable from standard data sheets, specification sheets, published advertising, and/or sales literature normally supplied by the manufacturers of the items bid.
B. Backbone Cable Requirements
The Contractor shall provide all of the expertise, labor, supervision, tools, materials, hardware and testing required to install copper and fiber backbone cabling conforming to TIA-568.
1. Conduit and Innerduct Systems
a) Where there is conduit present that may be used for the installation of telecommunications cable, the Contractor must receive written permission from the Authorized User to utilize that conduit. All fiber optic backbone cabling shall be installed in innerduct. Pull cords shall be provided in any conduits and innerduct used by the Contractor, whether or not the Contractor installed that conduit or innerduct.
b) Where the Contractor provides and installs innerduct, it must be corrugated, one inch (1”) in nominal diameter and orange in color, unless otherwise requested in writing by the Authorized User. Innerduct may be provided in other colors and smaller diameters if requested in writing by the Authorized User, provided the price does not exceed the price bid herein for one inch (1”) innerduct. Other types of innerduct systems may also be utilized where specified in writing by the Authorized User.
2. Copper Backbone Cable
a) The Contractor shall install backbone cabling conforming to TIA-568 Category 3,
Category 5e, Category 6, Category 6A, or other TIA-568-compliant cabling as required by the Authorized User for the specific project at hand.
b) The Contractor shall provide riser-rated, plenum-rated, direct-burial, underground or other appropriately-rated cable with a pair count of up to 300 pairs per cable as required by Authorized User and applicable codes. Where more than 300 pairs of backbone cable are required, multiple large pair-count cables or single cables with larger pair counts shall be used.
c) All backbone cabling and associated hardware shall be documented, labeled and colorcoded in keeping with TIA-606 and, at the Authorized User’s request, to conform to the site’s existing labeling scheme. All cable pairs shall be tested and certified to perform in accordance with the applicable TIA standard(s), and documentation of the system design and performance shall be presented to the Authorized User upon completion of work.
d) The cables shall be terminated at the Authorized User’s option onto 110- or 66-type cross connection hardware or 110-to-RJ45 patch panels manufacturer-rated to meet or exceed the performance category of the corresponding backbone cable. Termination hardware (connecting blocks and/or backbone patch panels) shall be mounted onto fire retardant or fire resistant ¾” plywood panels mounted on the walls of the appropriate spaces in each building. Backbone patch panels may, at the Authorized User’s option, be mounted on Authorized User-provided distribution racks or, in the absence of space on existing backbone distribution racks, Contractor-provided 19” racks. Where grounding is necessary, all cables, pathways and hardware shall be properly grounded in accordance with TIA-607 and all applicable electrical and fire codes.
3. Optical Fiber Backbone Cable
a) The Contractor shall provide, install and test 62.5/125 micron multimode optical fiber cable and/or 850nm laser-optimized 50/125 micron multimode optical fiber cable and/or singlemode optical fiber cable in innerduct as required by the Authorized User. The innerduct and fiber cable shall be rated for riser, plenum, direct-burial or other appropriate underground use as required by the Authorized User and applicable codes for the application at hand. The innerduct in which the cable is installed shall extend into the cabinet housing the fiber terminations at each end.
b) A minimum of 15 feet (15’) of slack shall be coiled in the cabinet (or a separate enclosure designed for this purpose) at each end to allow for future re-termination, relocation, etc. Every fiber shall be terminated using 568SC (duplex SC) connectors (or other duplex small form factor connectors complying with TIA-568 as requested by the Authorized User) in either a wall-mount fiber cabinet or a rack-mount fiber cabinet at the option of the Authorized User. The Authorized User must agree to any deviations from this configuration in advance of start of work and in writing. All fiber cabinets must include all hardware necessary to properly mount, mate and align the associated backbone fiber connectors with the appropriate patch cord connectors.
c) The Contractor shall provide optical fiber patch cord(s) appropriate to the backbone fibers installed complying with TIA-568 in the quantities and lengths requested to be used with the Contractor-installed backbone links. Hybrid patch cords shall be supplied where required for interfacing to end equipment with non-duplex SC (568SC) connectors. A dust cover/dust cap shall protect each connector not physically connected to a patch cord or equipment cable.
d) All innerduct, fiber cabling, cabinets, connectors, and supporting hardware shall be provided by the Contractor and installed according to all applicable standards and the manufacturer’s recommendations.
e) All optical fiber cabling, connectors, and hardware shall meet the minimum performance standards of, and be installed, terminated, and tested as specified in TIA-568. Testing shall be performed in accordance with and pass the requirements of TIA-568. Certified documentation of the passing test results showing all test parameters shall be presented to the Authorized User upon completion of work.
C. Telecommunications Room (TR) Requirements
1. Backboards – When backboards are recommended by industry standards or requested by the Authorized User, provide and install 8-foot tall by 4-foot wide trade size ¾ AC-grade voidfree plywood backboards painted with a light-colored fire-retardant paint. The Authorized User must agree to any deviation from this standard board size in writing in advance. The boards shall be either fire-rated or treated on all sides with at least two coats of fire-resistant paint. Use flush hardware and supports to mount the plywood, ensuring that the strength and placement of the hardware are sufficient to handle the total anticipated load and mounting of cabling and components.
2. Distribution Racks – When distribution racks (equipment racks) are recommended by industry standards or when they are requested by the Authorized User because sufficient space is not available in the existing distribution racks for wiring being installed under this Contract, provide and install racks designed for standard 19” TIA/EIA mounting. Contractor shall supply racks both approximately seven feet (7’) tall and three to four feet (3’ – 4’) tall. Racks shall be properly grounded, and anchored to the floor unless otherwise requested by the Authorized User. Contractor shall also supply swing-out (hinged/pivoting) wall-mount racks 35 to 48 inches (35” – 48”) tall and capable of supporting at least 100 pounds of equipment and cables.
3. Patch Panels - All UTP patch panels specified in this document shall consist of a modular (RJ45) front to 110-type back connector system and shall be fully populated (all ports occupied by jacks). The panels shall incorporate sufficient cable support and/or strain relief mechanisms, including rear cable management/strain relief bars, to secure the horizontal cables at the termination block and to ensure adherence to all manufacturers’ and standard minimum bend radius specifications.
4. Cable routing – All station cable located in the TR shall be loosely bundled. Cable shall be routed along ladder rack or functionally equivalent cable tray when patch panels are rackmounted. When patch panels are wall-mounted, cable traversing floor space shall be routed along ladder rack or functionally equivalent cable tray, while cable routed vertically along walls shall be routed using ladder rack, “D” rings, hook-and-loop type routing hardware or other re-enterable routing hardware.
5. Patch cable management – Provide and install in all Contractor-provided equipment rack(s) front-side wire management hardware consisting of at least four (4) three-inch (3”) rings above and below each patch panel for horizontal patch cord routing, as well as side-mounted rings, channels, or equivalent retention hardware for vertical cable management.
6. Patch panel administration – The ports on the patch panels shall be labeled according to TIA606 unless otherwise requested by the Authorized User. If so requested by the Authorized User, separate patch panels shall be used for each floor or zone of the office space being cabled.
7. Patch cords – The Contractor shall supply manufacturer factory-terminated patch cords/work area cables which meet or exceed Category 5e, Category 6 or Category 6A specifications for patch cords as specified in TIA-568 for Category 5e, Category 6 and Category 6A copper cable runs installed (respectively), in the quantities specified by the Authorized User. Where the user requires
patch cords as part of an overall cabling installation, Contractor shall supply cords of a sufficient length to allow neat and orderly patching between any two port positions based upon the rack layout agreed upon per number 8 below, but a minimum of three feet (3’) in length.
8. Drawings – After execution of an order and before start of work, the Contractor shall submit for the Authorized User’s approval a detailed drawing/diagram of each TR showing the exact locations/layout of all racks, equipment, cabling, and supporting hardware to be provided under the Contract. Detail drawings of each rack showing dimensions and placement of all patch panels, cable/cord management hardware, etc. within each rack shall be included.
D. Horizontal Cabling Requirements
1. All copper wiring and cabling which terminates in work areas shall be installed and terminated in such a manner as to be fully compliant with the TIA-568 standard for Category 5e, Category 6 or Category 6A UTP wiring, or other TIA-568-compliant wiring as specified in writing by the Authorized User, and shall conform to the standard eight-position jack pin/pair assignment designated T568A or T568B. The T568B pin/pair assignment may only be used when all preexisting cabling in the building being cabled is wired per T568B, or when the Authorized User has standardized on, and requested in writing, T568B. In those cases, the Contractor shall ensure that all equipment racks and patch panels used for such cable terminations bear a sign clearly reading, “ATTENTION: PIN-OUT T568B IN USE,” unless otherwise requested in writing by the Authorized User.
2. The Contractor shall be required to provide a printout certifying each horizontal cable run as compliant with the TIA-568 specifications for the Category of cable link and/or channel under test (as appropriate) via an electronic testing device specifically designed for that purpose, according to all applicable manufacturers’ instructions and recommended configurations. Cable certification printouts must show all relevant parameters for the category of cable under test and the relative performance of the particular link being tested, as well as an overall pass/fail rating. Improperly performed tests will not be accepted, including tests performed where the Nominal Velocity of Propagation (NVP) is not properly configured for the specific cable under test. All test results shall be provided in both electronic format and hard copy. Hard copies shall be sorted by cable ID and shall consist of no more than two cable test reports per page. Each page shall be signed and dated by the Contractor’s responsible representative certifying that the link passed the test and that the test was performed in accordance with applicable standards and manufacturer’s instructions.
3. For each work area requested by the Authorized User, the Contractor shall provide up to eight (8) four-pair Category 5e, Category 6, Category 6A, or other specified TIA-568-compliant cables originating at the Contractor-provided patch panels in the appropriate TR and terminated on appropriate corresponding RJ45 telecommunications outlets/connectors (“jacks”) mounted in an appropriately-sized faceplate at the work area. All cables shall be “home-run” (one continuous cable segment from TR to work area telecommunications outlet/connector) except as allowed otherwise herein.
4. Regardless of the number of jacks required in each work area, each Contractor-provided faceplate shall have at least three (3) ports. Wall-mounted faceplates shall be of a color agreed upon by the Authorized User to match the décor of the offices being cabled. Every jack shall be labeled according to TIA-606 unless otherwise requested by the Authorized User. For all faceplates, any ports not populated with jacks shall be fitted with blanks.
5. For each wall telephone jack requested by the Authorized User, the Contractor shall provide one (1) four-pair Category 5e, Category 6, Category 6A, or other TIA-568-compliant cable specified in writing by the Authorized User, originating in the appropriate TR and terminated on a
standard wall telephone jack mounted 48” above finished floor and in compliance with the Americans with Disabilities Act.
6. All plenum-rated cables shall be insulated 100% with FEP, and all suspension hardware and cable management materials installed within environmental air handling plenums shall be plenum-rated according to applicable codes. Non-plenum-rated cables and hardware shall be used only when they comply with all codes and are requested in writing by the Authorized User.
7. All cables shall be installed so as to be fully concealed within ceilings, walls and columns, and fished into modular furniture as required. All work area telecommunications outlets/connectors shall be in flush-mounted faceplates. Data/power poles shall be used only when there is no other feasible method of routing and concealing cables. Where it is not practicable to fish walls or otherwise conceal cable in ceilings and walls, the Contractor may use a Category 6A compliant surface raceway system and matching surface-mount outlet box, if applicable. Any poles or surface raceway systems installed by the Contractor must be approved in advance by the Authorized User to ensure that it is compatible with space plans and office décor.
8. Cable support hardware installed above suspended ceilings may not be mounted on or in any way supported by the ceiling grid, panels, support channels, or vertical ceiling supports such as ceiling support wires or rods. All cables routed above ceilings shall be suspended in keeping with all applicable standards and supported within conduit, cable tray, “J” hooks, or functionally equivalent open-top support systems. Cables shall not sag more than 12” between cable supports. Of course, TIA standards for spacing, routing, and cable sag shall be followed. Cables shall be loosely bundled and follow hallways and common areas and be installed in keeping with TIA recommendations.
9. Each Contractor-supplied horizontal cable shall incorporate a minimum of six feet (6’) of “service slack” located in the TR, plus enough additional cable length to allow any cable to be relocated within the patch panel while still maintaining the minimum six feet of slack.
10. The Contractor shall, at the request of the Authorized User, supply color-coded horizontal cabling and jacks to facilitate distinguishing between cables of different categories or cables intended for different purposes. A minimum of three (3) distinct colors of horizontal cabling, patch cables and matching jacks/inserts shall be made available for each category of cable.
11. The Contractor shall label each element of the cabling system according to TIA-606 using the appropriate administration class, unless otherwise specifically instructed by the Authorized User. Where horizontal cables terminate in wall boxes at the work area, their labels shall be located within the wall boxes.
12. All components shall meet all applicable building codes and requirements.
13. When requested in writing in advance by the Authorized User, the Contractor shall supply cabling for open office spaces to include multi-user telecommunications outlet assemblies (MUTOAs), consolidation points (CPs), and transition points (TPs). Any open office-type cabling systems shall be installed according to the applicable TIA standards.
E. Miscellaneous Cabling Services
Miscellaneous cabling services shall include, but not be limited to, the field testing, documentation, labeling, cross-connecting, reconfiguring, troubleshooting and repairing of previously installed cabling systems.
F. Abandoned Cable
The Contractor shall, at the request of the Authorized User, remove “abandoned” telecommunications cable from building pathways and spaces. Abandoned cable is defined as installed cable that is neither terminated at both ends at a connector or other equipment, nor identified for future use with a tag. Abandoned cable may only be removed at the direction of the Authorized User or to avoid a code violation. The Contractor shall notify the Authorized User in writing of the presence of any abandoned cable that is in violation of the National Electric Code.
G. As-built Drawings
The Contractor shall maintain in good order for the duration of work at each site one complete set of as-built plans supplied by the Authorized User. These plans shall be used for reporting any changes made during the job and to denote exact locations of equipment, cable routing, terminations, and outlets. The plans shall be kept up-todate always as the work progresses and as any changes occur. At the completion of the work, this set of plans shall be turned over to the Authorized User as a permanent record.
H. System Acceptance and Performance Requirements
1. Upon completion of a work order or SOW under this Contract, the Contractor shall notify the Authorized User for the purpose of scheduling a joint inspection of the work. No acceptance period shall begin until after the Authorized User has been given an opportunity to perform a thorough inspection of the completed work.
2. Each system may be accepted by the Authorized User in accordance with the order or SOW, after the Contractor satisfies the order or SOW requirements, including, but not limited, to the following:
a) Delivery and installation of all required equipment and material
b) Delivery of all required documentation, including all passing cable test results as recommended by TIA-568 and other applicable TIA standards.
c) Successful completion of performance period
3. A performance period of thirty (30) consecutive calendar days of twenty-four (24) hours each wherein the system operates without a failure shall constitute a successfully completed performance period.
I. Delivery and Storage
1. The Contractor shall be responsible for making the arrangements for the delivery, unloading, and storage of materials and equipment required to install cabling systems.
2. The Authorized User will assume no responsibility for receiving any equipment and/or materials shipped to the Authorized User’s premises by or on behalf of the Contractor.
3. No space will be available for long-term storage of material and/or equipment.
4. In providing storage for the convenience of the Contractor, the Authorized User assumes no responsibility for items that may be lost, stolen, misplaced, damaged, or destroyed.
J. Quality of Work
1. All equipment, cables, wiring, outlets, etc., shall be installed in a neat and orderly manner.
2. The Contractor shall assign only competent supervisors, technicians, and laborers to work on projects initiated under this Contract.
3. Services shall be performed by fully-qualified individuals with all training and/or certification(s) required by the manufacturer(s) of the products they are installing or using, as applicable.
4. Upon receipt of written notification from the Authorized User, the Contractor shall immediately relieve any person(s) determined to be incompetent or disorderly of all responsibilities for further on-site work and/or contact with the Authorized User for the duration of this Contract.